	Project No:
	A511
	NCR No:
	2

	Project Name:
	Gold Coast Secure Mental Health Unit
	Date:
	14/05/24

	Issued by:
	Ross Snelgrove
	Issued to:
	Padstar

	Title
	Damage to protective coatings due to installation of safety mesh

	Trade
	Roofing 

	Description of 
Non-Conformance
	The roof structure is designed with PFC’s trimming the perimeter of the roof. As roof safety mesh needs to be fixed to these perimeter members the subcontractor has drilled through the flange of the PFC. This was selected in line with AS/NZS 4389:2015 as opposed to the alternative methods which would have resulted in greater damage to the protective coatings.

Due to the action of drilling these holes some damage to the PFC protective coating/minor surface rust has occurred. 

	Location / Area
	PFC’s trimming the Lower Ground roof structure

	Root Cause
	Process: Design Issue. Safety mesh not considered in design 

	Respond By 
	May 2024


	Proposed Remedial Action
	Touch up any damaged protective coatings with the suppliers recommended site repair product to reinstate the durability. 


	Preventive Action
	As the safety mesh needs to extend to the perimeter of the roof structure, holes will continue to be drilled into the PFC flange. Protective coatings will be inspected & touched up as required prior to concealing with roof sheeting. 





