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Inspection Template: ITP: Passive Fire 03.36 

Fire Doors / Frames / Hardware 

 Confirm manufactures door set is compliant with tested wall system: Upload Manufacturer’s specification and test results 
 	  
Fire rating / filling requirement of frame: Manufacturer's specification / AS 1905.1 

Correct fire rated frame installed plumb and level: Check frame filled and 25mm stop on frame 

Frame sealed to floor substrate: Upload photos 

Fixings installed as per Manufacturer's recommendations including size / gauge and distances: Upload photos 

Doors only measured after floor finish installed or written agreed heights with floor and door subcontractors: Upload written agreement                                                correspondence to subcontractors here 

Door and hardware only installed by licensed carpenter as per BCA: Upload license here 

Caps to door / frame/ floor checked and compliant with Manufacturer's tested system: Specify gaps here as per AS1905.1 or         manufactures test requirement 

Doors and frames inspected and tagged: Upload all applicable documents here 

Walls & Ceilings 

 Framing installed with Noggins and corner angles: Upload details and photos, No timber allowed in fire walls 
 	  
      Seismic fixings installed: As per AS 1170.4: Upload photos 

Wall junctions as per Manufacturer's detail: Upload photos 

      Sarking installed has Flammable index and identification facing inwards AS1530.2: Upload photos 

Fire boxes installed in walls: Upload photos, upload Manufacturer's data 
	  


       Ceiling framing as per Manufacturer's system for fixings: Upload photos 
 	  
Base Metal Thickness (BMT) of framing as per tested system: Check against tested system requirement 

Sheet joints staggered: Upload photos showing distances 

Vertical and horizontal fire separation as per NCC-2.6: Upload photos 

Rockwool installed to U/S roof sheeting and/or cavities: Upload photos 



       Fire walls complete and ready for McNab inspection before sheeting

All fixings and joints are set: Upload photos 

All sheeting abutting other surfaces is fire rated/ sealed: Upload photos 

Services Penetrations 

 Sample board set up and approved for all fire rating requirements: Arrange 3rd party inspection with Quality 
 	  
Fire collars and wraps have a current test certificate: Upload current test certificates 

Fire mastics have current test data and are compliant with test: Upload current test certificates 

Services are minimal 100mm from combustible surface: Upload photos 

Fire penetrations inspected and sticker attached: Upload photos and register 

	  
Setting sub-contractor

[bookmark: _GoBack]       Joints taped, base coat, top coat complete (Photos attached).

Walls and ceilings sanded, free of blemishes ready for sealer coat.

Floors Scraped units cleaned (photos required).

(HOLD POINT) Inspection with McNab ahead of the painter.
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